|  | CAIRNS WATER PRE-COMMISSIONING CHECKLIST FOR NEW ASSETS |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | WATER SITES |  |  |  |  |
| REQUIREMENTS BY CONTRACTOR |  |  |  |  |  |
| The following checklist is required to be fully completed, signed and returned to Cairns Water before a joint commissioning is considered. Please note: in the event of a commissioning being abandoned due to works not completed or operational, Cairns Water will recover costs incurred. SITE NAME RESERVOIR: SITE NAME P/S: |  |  |  |  |  |
| - Ergon Power available |  | Yes |  | No |  |
| - Provision of sufficient water for all testing purposes |  | Yes |  | No |  |
| - Fresh water discharge flushing system operating as per design |  | Yes |  | No |  |
| - Ancillaries (GPO's, lighting etc) tested and working correctly |  | Yes |  | No |  |
| - Pre commission switchboard test completed |  | Yes |  | No |  |
| - Station telemetry points list supplied |  | Yes |  | No |  |
| - Established telemetry communications and verified inputs locally |  | Yes |  | No |  |
| VERIFICATION OF AS CONSTRUCTED LEVELS AND OPERATION. |  |  |  |  |  |
| Note: Levels taken from floor level |  |  |  |  |  |

| Setting/Alarm | Measurement | Operational function (contractor to verify correct operation) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Overflow level | m |  |  |  |  |
| High Level alarm | m | Yes |  | No |  |
| Fill stop level | m | Yes |  | No |  |
| Fill request level | m | Yes |  | No |  |
| Low level alarm | m | Yes |  | No |  |
| Very Low Level Alarm | m | Yes |  | No |  |
| Level settings according to design |  | Yes |  No � | NA | � |

Commissioning of Civil Works

| Item |  |  | Complete | Date / Initials | Council Audit |
| --- | --- | --- | --- | --- | --- |
| Management |  |  |  |  |  |
| 1. |  | Verify that consultant has provided all documentation. (as constructed details, operating manuals, test results etc) | ❑ |  |  |
|  |  | If NO then close audit. | ❑ |  |  |
| Concrete |  |  |  |  |  |
|  | Verify that there is no damage to any exposed concrete surface. |  | ❑ |  |  |
|  | Verify that drainage of the site is away from the structures. |  | ❑ |  |  |
|  | Verify that the below ground concrete structures are dimensionally correct and in accordance with the design drawings. |  | ❑ |  |  |
|  | Verify no seepage through the concrete structure. |  | ❑ |  |  |
|  | Verify the verticality of the structure is within tolerance in accordance with SEWL specifications. |  | ❑ |  |  |
|  | Verify that all chamfers are provided in accordance with the design drawings. |  | ❑ |  |  |
|  | Verify that the specified coating to the internal walls has been applied in accordance with the FNQROC Development Manual. |  | ❑ |  |  |
|  | Thickness of internal coating tested (µm) |  | ❑ |  |  |
| OH&S |  |  |  |  |  |
|  | Verify that ladder access meets OH&S requirements. |  | ❑ |  |  |
|  | Verify that access to valve chamber meets OH&S requirements. |  | ❑ |  |  |
|  | Verify that all ladders are provided with the extension above the FSL. |  | ❑ |  |  |
|  | Verify that the ladders have non-slip treads. |  | ❑ |  |  |
|  | Have safety cages been specified in accordance with Australian Standards. |  | ❑ |  |  |
|  | Verify that safety cages have been installed in accordance with the design drawings. |  | ❑ |  |  |
|  | Verify that adequate set down areas for the covers has been provided in accordance with OH&S requirements. |  | ❑ |  |  |
|  | Verify that no overhead cables restrict access via crane trucks. |  | ❑ |  |  |
|  | Verify Full Risk Assessment has been performed and permanent operational/ maintenance risks identified |  | ❑ |  |  |
|  | Verify that all signage pertaining to those risks is in place |  | ❑ |  |  |
|  | Facility Name and contacts signage |  | ❑ |  |  |
|  | Standby Emergency Generator – cover, refueling, manuals |  | ❑ |  |  |
|  | Adequate access, maneuver and parking for maintenance vehicles |  | ❑ |  |  |
| 14. | Switchboard access and clearance meets requirements under Electrical Safety Act |  | ❑ |  |  |
| 15. | Personnel/maintenance access ring install in side wall of reservoir |  | ❑ |  |  |
| Products & Materials |  |  |  |  |  |
| - Verify that all products incorporated on the project are included on the list of approved products for Cairns Regional Council. |  |  | ❑ |  |  |
| - Verify that all markings as required by Cairns Water specification are visible on the covers. |  |  | ❑ |  |  |
| - Verify that the covers and frames are greased in accordance with the manufacturer’s requirements. |  |  | ❑ |  |  |
| - Verify that the interchangeable multi part covers have lifting lugs on the beams for removal and covers have clockwise lifting key holes. |  |  | ❑ |  |  |
| - Verify that internal ladders are stainless steel. |  |  | ❑ |  |  |
| Pipes and Fittings |  |  |  |  |  |
| - Verify that the valves are anticlockwise closing. |  |  | ❑ |  |  |
| - Verify that adequate supports have been provided for the valves. |  |  | ❑ |  |  |
| - Are valve extension spindles required. |  |  | ❑ |  |  |
| - Verify that there is sufficient clearance for maintenance. |  |  | ❑ |  |  |
| - Are adequate supports provided in accordance with Cairns Water standard drawings. |  |  | ❑ /NA |  |  |
| - Verify that DICL pipe work has been provided to correct nominal diameter DN. |  |  | ❑ |  |  |
| - Verify that adequate supports for vertical pipe work has been provided in accordance with FNQROC Development Manual. |  |  | ❑ |  |  |
| - Verify that all gate valves operate through the full range and are left in the open position. |  |  | ❑ |  |  |
| - Verify that a flap valve has been installed on the valve chamber drain if required by the design. |  |  | ❑ |  |  |
| - Verify that the Cairns Water specified coating for all valves has been applied. |  |  | ❑ |  |  |
| - Verify that the Cairns Water specified coating for the pipe work has been applied. |  |  | ❑ |  |  |
| - Verify that the specified bolting system on the flanges has been used. |  |  | ❑ |  |  |
| - Verify that all valves can be removed through the available cover opening. |  |  | ❑ |  |  |
| - Verify that a flanged dismantling joint has been provided to allow ease of removal of valves in accordance with standard drawings. |  |  | ❑ |  |  |
| - Has the consultant submitted completed project ITP containing all signatures. |  |  | ❑ |  |  |
| - Verify all steel metalwork has been Hot Dipped Galvanized. |  |  | ❑ |  |  |
| - Verify all bolts are 316 stainless steel with 308 nuts. |  |  | ❑ |  |  |
| Other Services. |  |  |  |  |  |
| - Verify that the water service has been fitted with an approved back flow prevention device. |  |  | ❑ |  |  |
|  |  |  | ❑ |  |  |
| - Verify that all conduits through the walls have been sealed. |  |  | ❑ |  |  |
| - Verify that electricity is below ground, not above. |  |  | ❑ |  |  |
| - Verify that the sealed access track is in accordance with the design drawings and the FNQROC Development Manual. |  |  | ❑ |  |  |
| - Verify that adequate site drainage has been provided. |  |  | ❑ |  |  |
| Restoration. |  |  |  |  |  |
| - Verify that the site restoration has been completed. |  |  | ❑ |  |  |
| Testing. |  |  |  |  |  |
|  |  |  | ❑ |  |  |
|  |  |  | ❑ |  |  |
|  |  |  | ❑ |  |  |
| Mechanical Equipment. |  |  |  |  |  |
|  |  |  | ❑ |  |  |
|  |  |  | ❑ |  |  |
| Electrical Equipment. |  |  |  |  |  |
| - Verify identification plates has been fitted to the electrical cabinet. |  |  | ❑ |  |  |
| - Verify that the telemetry antenna has adequate protection in accordance with Cairns Water specification. |  |  | ❑ |  |  |
| - Verify that lighting within the switchboard has been provided. |  |  | ❑ |  |  |
| - Verify that the Cairns Water locks fitted to switchboard and operational. |  |  | ❑ |  |  |
| - Verify that quick link generator connectors provided if applicable. |  |  | ❑ |  |  |
| Security. |  |  |  |  |  |
| - Verify that the security fencing has been installed in accordance with the design drawings. |  |  | ❑ |  |  |
| - Verify that Cairns Water keyed locks installed. |  |  | ❑ |  |  |
| - Verify that the switchboard meter cabinet has been fitted with Ergon Locks. |  |  | ❑ |  |  |
| - Have all NCR items been resolved (including any raised as a result of this audit)? |  |  | ❑ |  |  |
| If YES Issue Acceptance of Works., and close audit. |  |  | ❑ |  |  |
| Would outstanding NCR items impact on the ability to operate the pump? |  |  | ❑ |  |  |
| If YES then close audit (wait for NCRs to be resolved). |  |  | ❑ |  |  |
| Has Operations authorized the pumps to remain on? |  |  | ❑ |  |  |
| If YES record the name of the person who authorized this. NAME…………………………………. |  |  | ❑ |  |  |